Town of Dover

Sewage Ordinance

Adopted:	June 10, 1975

Amended:	October 9, 1990

February 4, 1997

October 7, 1997

1000.

2000.

3000.

4000.

5000.

6000.

7000.

8000.

9000.

TOWN OF DOVER SEWAGE ORDINANCE INDEX

PURPOSE

DEFINITIONS

APPLICABILITY OF ORDINANOE

3100.	 Seasonal Dwellings

3200.	 Single Family Residential Structures

3300.	 Multiple Family Residential Structures

3400.	 Commercial & Industrial Structures

3500.	 Change of Use

3600. 	Replacement systems

3700. 	Other Applicable Regulations

APPLICATION FOR PERMIT

4100. Disposal System Construction Permit

4200. Limited Permits

4300. Plan Filing

4400. Minor Permit

4500. Certificate of Compliance

4600. Recertification of Permits

4700. Terms & Conditions of Permits

4800. Revocation of Permits

TECHRICAL 5100. 5200. 5300. 5400. 5500. 5600. 5700. 5800. 5900.

INFORMATION

Occupancy Definitions and

Soil and Site Evaluations

Septic Tanks

Sewage Drains

Distribution Boxes

Leaching Facilities

Required size for Leaching Trenches & Beds Water Saving Devices

Pumps

Regulations

ALTERNATIVE SYSTEMS & PERMITTED DEVIATIONS

APPEALS

ENFORCEMENT

SEVERABILITY

First adoption by the Dover Board of Selectmen: 10 June 1975 Adoption of State suggested Amendments by Board: 16 September 1975 Approval by State Board of Health: 14 October 1975

Updated by the Board of Selectmen: 09 October 1990

Adoption of State suggested Amendments by Board: 04 February 1997 Approval by State Board of Health: 18 February 1997

Adoption of suggested Amendments by Board: 7 October 1997

Approval by State Board of Health: 23 October 1997

Adoption of State suggested Amendments by Board:

Page 2

Dover Sewage Ordinance

2000. Definitions

Minor Modification: Generally understood to be work on or replacement of the septic tank or the piping between the septic tank or the pump chamber and the house. . The Sewage Officer shall decide what constitutes a minor modification on a case-by-case basis.

Permit. - A written authorization issued by the Town Sewage Officer.

Person: Any institution, public or Private Corporation,

individual, partnership, or other entity.

Sand:

The fill material from the natural soil plowed surface to the top of the trench or bed shall be sand texture with one of the following sieve analyses: Page 51, A, B, or C or the Small Scale Wastewater Treatment and Disposal Rules.

Seasonal Dwelling: A habitable structure, which has no running water, or plumbing and is not occupied for more than six (6) months of the year.

Sewage Disposal System: System for disposal of waste using undisturbed soil on-site as a disposal medium, including a tank for collection of solids and leaches area for liquids, or any other system, which disposes of wastewater on site. This shall include multiple family, commercial and industrial on-site disposal systems, as well as individual single-family homes and seasonal dwellings.

Sewage Officer: The legally designated authority of the town acting under the authority of this ordinance. The Board of Selectmen shall appoint the Sewage Officer. The Sewage Officer may be the town's Health Officer, Administrative Officer, or other town official.

Single Family: A group of persons related by blood or marriage or a group of persons unrelated by blood or marriage living together as a household.

Single Family Dwelling: Separate living quarters with cooking, sleeping and sanitary facilities provided within a dwelling unit for the use of a single family maintaining a household.

Wastewater System & Potable Water Supply Rules: Effective August 16, 2002 promulgated by the Vermont Department of Environmental Conservation. These rules are incorporated into this ordinance by reference.

Stone - clean or washed, hard stone, free from fines, 3/4" to 1½" in size.

Page 3

Dover Sewage Ordinance

3000.

3010.

3020.

3030.

3100.

3110.

3120.

3130.

APPLICABILITY OF ORDIRANCE

All individual or community (except municipal) sewage disposal systems shall be built, altered, repaired, and used in accordance with this ordinance, and only after a permit has been issued by the Sewage Officer. This includes, but is not limited to, sewage disposal systems for seasonal dwellings, single and multiple family homes, and commercial and industrial properties.

If a building wasteline has not been connected to a municipal sanitary sewer, or duly approved group or community system, the building wasteline shall be connected to a sewer system that complies with the provisions of this ordinance.

In the case of any applicable regulations, bylaw ordinances or statutes that differs from this ordinance, THE STRICTER SHALL APPLY.

SEASONAL DWELLINGS ( CAMPS)

Any dwelling constructed after the enactment of this ordinance must receive a Disposal System Construction Permit meeting the full minimum standards of this ordinance if the useful occupancy of the dwelling requires running water. The use of any seasonal dwelling shall not be changed until the requirements of Change of Use (Section 3500), et sequencia, are met.

All seasonal dwellings which will not have plumbing and which shall have no running water at anytime, and shall have no pumping of water into the dwelling, do not need a Disposal System Construction Permit. These seasonal dwellings shall receive a minor permit from the town prior to commencement of construction on the property.

A seasonal dwelling constructed prior to enactment of this ordinance shall not be required to have a sewage disposal system provided no health hazard, nuisance or surface or ground water pollution exists. The Sewage Officer or Health Officer shall determine if such conditions exist. If such conditions exist, a disposal system shall be installed and upgraded to meet the standards of this ordinance to the extent possible or the running water shall be removed and the generation of sewage ended.

Page 4

Dover Sewage Ordinance

3200.

SINGLE FAMILY RESIDENTIAL STRUCTURES

All single-family residences shall receive a Disposal System Construction Permit before commencement of construction on the property. Construction shall be understood to mean the construction, reconstruction, conversion, structural alteration, relocation or enlargement of any structure, including foundation excavation, foundation or building construction, and shall include site work which involves or may affect any portion or existing or proposed sewage disposal or water supply facilities for the structure, and any change in the use of any structure.

3210.      SINGLE FAMILY RESIDENTIAL STRUCTURE DISPOSAL SYSTEM

ALTERATIONS

3220.

3300.

3310.

3320.

No sewage disposal system shall be altered, repaired, or rebuilt in any way, except as provided in Section 3220 Exception - Minor Modifications until a Disposal system Construction Permit has been issued.

EXCEPTIONS:

MINOR MODIFICATIONS

When a minor modification (see definitions) to an existing system for a single family dwelling is proposed, the Sewage Officer may waive the Disposal System Construction Permit requirement on a case-by-case basis and issue a minor permit. The Sewage Officer will determine what constitutes a minor modification.

MULTIPLE FAMILY DWELLINGS (Including Duplexes)

All multiple family dwellings shall submit an approved water supply and wastewater disposal state permit before commencement of construction on the property. In addition, a Town Disposal System Construction Permit must be obtained before commencement of construction. The applicant may submit design plans approved by the State for the Town's Disposal System Construction Permit providing that the plans meet the requirements of this ordinance.

All multiple family dwellings shall obtain a Certificate of Compliance as required by Section 4500 of this ordinance.

Sewage Ordinance

Page 5

3400.

3410.

3420.

3500.

3510.

3520.

3530.

3600.

3610.

3620.

COMMERCIAL AND INDUSTRIAL STRUCTURES

All commercial and industrial structures shall submit an approved water supply and wastewater disposal State permit prior to commencement of construction on the property. In addition, a Town Disposal System Construction Permit must be obtained before commencement of construction. The applicant may submit design plans approved by the State for the Town's Disposal System Construction Permit providing that the plans meet the requirement of this ordinance.

All commercial and industrial structures shall obtain a Certificate of Compliance as required by Section 4500 of this ordinance.

CHANGE OF USE

Change of use shall include, but is not limited to, the addition of plumbing or running water, the addition of bedrooms, any additional square footage to the structure , conversion of seasonal dwellings to single multiple family residential structures, conversion of single family residential structures to multiple or commercial or industrial use.

No structure, except those served by the North Branch Fire District, shall be altered in any way as to change the use of the structure until the Sewage Officer is satisfied that the existing sewage disposal system is adequate for the proposed use or a Sewage Disposal System Construction Permit has been issued for the proposed use.

No structure, except those served by the North Branch Fire District, shall be altered in any way so as to change the use of the structure unless the sewage disposal system and all proposed alterations meet the minimum standards of this or any other applicable State or local ordinances.

REPLACEMENT SYSTEMS

Before the failed system is replaced, it is important that the cause of the failure be determined to assure that a subsequent failure is avoided.

A Disposal System Construction Permit must be obtained prior to installing a replacement system. A Certificate of Compliance must be obtained within a reasonable period of time following the commencement of the installation of the system.

Sewage Ordinance

Page 6

3630.

3640.

3650.

3700.

4000.

4100.

4110.

4130.

Existing single-family dwelling sewage disposal systems in operation at the time of adoption of this ordinance are approved, provided that such systems do not create a health hazard, nuisance or pollute surface or groundwater. The Sewage Officer shall determine whether an existing system is causing a health hazard, nuisance or is polluting surface or groundwater. Existing systems determined to be a health hazard, nuisance or polluting surface or groundwater shall be upgraded to meet the standards of this ordinance to the extent possible.

Replacement systems for single family homes which have an approved replacement o~ continuous area shall be installed in the approved area in accordance with the original permit issued unless a new location meeting the current standards can be approved. The replacement septic system, shall at a minimum, meet the standards in effect when the 'original system was -permitted. Applicants are encouraged to take advantage of improved technology, if applicable.

Replacement systems for multiple family dwellings and commercial and industrial structures shall be constructed in accordance with relevant state and local regulations or ordinances. An approved state permit shall be submitted and approved by the Sewage Officer, prior to commencement of construction of the replacement system.

OTHER APPLICABLE REGULATIONS

In case of any applicable regulation, bylaw, ordinance or statute, which differs from this ordinance, the stricter authority shall prevail.

APPLICATION FOR PERMIT

DISPOSAL SYSTEM CONSTRUCTION PERMIT

Before commencement of construction, as defined under Section 3200, a person shall complete an application for a Sewage Disposal System Construction Permit on the prescribed form and submit it, accompanied by a fee, to the Sewage Officer.

The owner of any property, the useful occupancy of which requires a sewage disposal system, shall apply for a Disposal System Construction Permit. The owner of any property on which a sewage disposal system is proposed to be built, altered or replaced, shall apply for a Disposal System Construction Permit. The application shall contain soil and site information as required by this

Sewage Ordinance

Page 7

4140.

4145.

4146.

4150.

4200.

4210.

4220.

Ordinance and Wastewater System & Potable Water Supply Rules (see definitions) and a design for a disposal system and replacement system. Disposal system designs shall be' based on Table 1. (Section 5110) and Table 2 (Section 5710) Before construction occurs and prior to issuing a permit, site and soil conditions must be in compliance with the sewage ordinance. The system shall be designed as specified by the Vermont Health Regulations and as otherwise stated in this ordinance ( the more strict rules shall apply). No reduction in size of mound systems shall be permitted.

Technical information and tests for the application shall be prepared by a certified Site Technician B, or a professional Sanitary or Civil Engineer registered in the State of Vermont. The technical information must be submitted by the consultant to support their findings or recommendations.

The Town Sewage Officer shall review all Disposal System Construction Permit applications. The Sewage Officer shall review the plans and design recommendations for completeness and compliance with the minimum standards of this ordinance.

The Sewage Officer for an On-Site Disposal Permit must approve all state permits submitted for a town permit prior to approval.

Application Fees - the Board of Selectmen shall establish Application fees for permits.

LIMITED PERMITS

Site Modification - When site modification is necessary, the applicant shall first submit a tentative application and plot plan for development of the site, including the proposed modification of the site, floor plans for any buildings, and pertinent facts about the site that indicate there is a need for modification. Upon review, the Site Officer may issue a limited permit covering the minimum site modifications necessary to prove that the modified site will meet the requirements of this ordinance. No further construction may be done before the final Sewage Disposal System Construction Permit is issued.

Limited Permit Fee - A fee equal to the fee that applies to the completed system shall be paid at the time of filing the application. This fee shall be applied to the cost of the final permit.

Sewage Ordinance

Page 8

4300.

4320.

4330.

4340.

4350.

4360.

4370.

4399.

4400.

PLAN FILING

Two copies of the proposed plot plan with septic design and two complete floor plans, and a completed Disposal System Construction Permit Application (completed in triplicate) shall be submitted to the Sewage Officer. One copy with the Sewage Officer's final decision is to be returned to the applicant.

A proposed system shall be shown on the plot plan, detailing, separately, the location of each section of the system in relation to the dwelling to be served including the street, other lot lines, the source of water supply and the location of water lines.

All important dimensions, minimum and maximum, shall be shown including curtain and footing drain separation, brook and ditch separation, and detailing the distance of the water supply to the septic disposal areas.

One-foot (1') contour lines shall be used in the proposed system areas and for an area twenty-five feet (25' ) larger on all sides than the proposed systems. Scale shall be one inch (1") to twenty feet (20') or larger, and horizontal position shall be placed on all information submitted.

A lot location sketch shall be provided, showing enough information to easily find the lot within the Town of Dover. It is required that the tax map code and property owners name be placed on all information submitted.

Location of all soil excavation holes and percolation test holes shall be shown on the plot plan.

It is required that lots provide a suitable replacement area that meets the requirements of this ordinance, which could be used upon failure of the approved system. The replacement area must be shown on the plot plan, meeting all of the requirements of this ordinance.

If plans have no date, the Sewage Officer may deem them invalid and updated plans will be required.

MINOR PERMITS: SIMPLIFIED Application PROCESS FOR MINOR MODIFICATIONS AND STRUCTURES NOT REQUIRING A SEWAGE DISPOSAL PERMIT

The owner of any property intending to make a minor modification or construct a structure, the useful occupancy shall not require running water, shall make an application for a Minor Permit on the prescribed form.

Sewage Ordinance

Page 9

4500.

4600.

4610.

4620.

4700.

4710.

Such minor modifications shall not include changes of use. Vault or pit privies shall receive a minor permit prior to installation. Such application shall contain sufficient information to enable the Sewage Officer to evaluate the project. Application shall be made prior to commencement of construction.

,

CERTIFICATE OF COMPLIANCE

The Sewage Officer or his/her designee may, at his/her discretion, inspect all systems before they are covered with soil. The Sewage Officer may request to inspect the systems. The designer and installer of the approved sewage disposal system shall submit a Final Construction Report to the Sewage Officer on the prescribed form. Any variations from the approved design shall be noted in the report. The Sewage Officer shall issue a Certificate of Compliance when satisfied with the installed sewage system, and has received a Final Inspection Report. The newly constructed dwelling may not be occupied until the Certificate of Compliance has been issued. Existing dwellings, which require a replacement system may be occupied, provided a Certificate of Compliance is obtained within a reasonable period of time from commencement of installation of the system. The Sewage Officer shall decide what is a reasonable amount of time.

RECERTIFICATION OF PERMITS

Disposal System Construction Permits shall be recertified prior to expiring in order to retain the right to use the permit. Permits shall be recertified unless they are found to be based on false, fraudulent, or misleading information, or the original conditions of the permit can no longer be met, or the time limits specified in this or any other applicable state or local ordinances have expired.

Disposal System Construction Permits not recertified prior to expiration shall be deemed invalid. A new application must be made for a disposal system construction permit. The conditions of the ordinance in effect at the time of the application shall apply to this new permit.

TERMS AND CONDITIONS OF THE PERMITS

Conditions of construction or use may be placed on the Disposal System Construction Permit or the Certificate of Compliance.

Sewage Ordinance

Page 10

4720.

4730.

4800.

4810.

4811.

4812.

4814.

4820.

4821.

4822.

4830.

All permits run with the land and are binding upon each and subsequent owners. At the discretion of the Sewage Officer, all permits issued under this ordinance, or those permits with conditions of use issued pursuant to this ordinance, may be filed in the town land records.

Easements for off-lot sewage disposal systems must be conveyed to the permittee and recorded in the land records of both the conveyor and the permittee prior to issuance of the Disposal System Construction Permit.

REVOCATION OF PERMITS

The Sewage Officer for any of the following reasons may revoke a Disposal System Construction Permit, Minor Permit, Limited Permit or a Certificate of Compliance:

False, fraudulent, or misleading information contained in the permit application.

Installation of a system, which does not comply with the conditions of the permit.

Alteration of the proposed septic system site or replacement areas including effluent dispersion areas without prior approval of the Sewage Officer.

Failure to comply with this ordinance or any terms or conditions of permits issued under this ordinance.

Petition for Revocation A written petition for revocation shall be addressed to the Sewage Officer and shall set forth the name and address of the petitioner, the petitioner's interest in the matter, and a brief statement outlining the basis for revocation of permit, as per Section 4800.

The Board of Selectmen may file a petition participate in the revocation proceedings.

and

The Board of Selectmen shall notify the permit holder in writing of the petition for revocation within seventy-two (72) hours.

Receipt of the petition shall initiate the revocation procedure. The Board of Selectmen shall hold a hearing within thirty (30) days of the Sewage Officer receiving the revocation petition. The Board of Selectmen shall render a decision within fifteen (15) days of the conclusion of the hearing.

Sewage Ordinance

Page 11

4840.

5000.

5010.

5020.

5030.

5100.

5110.

The Sewage Officer shall give the permit holder written notice of the revocation of the permit with seventy-two (72) hours of revocation. All sewage disposal work must cease immediately upon notification of revocation of permit.

TECHNICAL INFORMATION

Technical information shall be prepared in accordance with the Wastewater System & Potable Water Supply Rules (see Definitions) and as specified below. Wastewater System & Potable Water Supply Rules shall be complied with except as amended below.

Soil and percolation tests are good for two (2) years from the date of the tests for use in submitting information for the Disposal System Construction Permit.

The system shall be approved and installed within two (2) years, otherwise the permits shall be deemed invalid, and new tests and a new permit, will be required (unless Section 4600 is applicable).

OCCUPARCY DEFINITIONS AND REGULATIONS

For purposes of these regulations, the number of people per bedroom shall be figured as follows:

Table 1.

Bedroom Size

Up to 200 sq. ft. 201 to 249 sq. ft. 250 to 320 sq. ft. over 321 sq. ft.

Number of Peop1e

2

3

4

6

5120.

5130.

5135.

For lofts without knee walls, only floor space having over two (2) feet headroom shall be counted.

For each unit, credit may be given for one (1) oversized master bedroom (not to exceed 320 sq. ft.) having only two (2) persons.

For each unit one room designated as a den/office, which may fall under the guidelines of a bedroom as specified in Section 5140, may be exempted if the total number of bedrooms exceeds four (4).

Sewage Ordinance

Page 12

5140.

5150.

5160.

5170.

5180.

5200.

5220.

5230.

5240.

5250.

5260.

In order to provide a system adequate for higher occupancies common to winter rental usage to which any house may be subject upon change of ownership or intentions of the owner's rooms which could be used as bedrooms shall be considered as bedrooms, regardless of the occupancy of the owner or intended owner.

A room in which a bed or bunk will not fit or which cannot offer privacy from the living areas of the dwelling unit need not be considered a bedroom.

Omission of a door, which can be easily mounted, shall not disqualify a room as a bedroom.

Closed lofts shall be considered regular bedrooms.

Open lofts shall be considered bedrooms, but only one half (1/2) of the space shall be counted.

SOIL AND SITE EVALUATION

A minimum of two (2) soil excavations shall be performed in each of the primary and replacement on site sewage disposal areas. The excavation holes shall be a minimum of seven (7) feet below ground surface or until an impermeable layer is encountered, whichever is greater. The seasonal high ground water table and depth to ledge shall be ascertained and documented.

The soil report shall be included and recorded with the final design recommendation made to the Town. The report shall include soil texture, density, structure, color, mottles, ledge and water seeps for each horizon, and the thickness of each horizon.

The Sewage Officer may request test pits to be done in his/her presence.

Where there are multiple beds or dependent trench groups, tests are required in each area.

To preserve the safety of persons and animals, if a soil test pit is left open after testing, it shall be covered with timbers and plywood, and shall be refilled within two (2) weeks.

The report of such tests and certifications that the location is suitable for the purpose intended shall be made part of the application.

Sewage Ordinance

Page 13

5270.

5280.

5290.

5300.

5310.

5320.

5330.

5340.

5350.

"Disposal Area" shall mean each individual disposal area, both primary and replacement. A minimum of two percolation tests shall be performed in both the primary and replacement area.

The thorough on-site soil identification shall be performed with a backhoe or similar equipment and soil excavations dug to seven (7) feet deep unless an impermeable layer is encountered. A hand soil auger shall not be utilized to identify the soils on-site.

The percolation rate shall be recorded as "minutes per inch". Copies of the field data for percolation tests, including date, type of tests .used, depth of hole, time intervals, drop in inches, and the final percolation result for each test hole recorded in minutes per inch shall be included on or with the plot plan.

SEPTIC TARKS

No steel tanks may be used.

All septic tanks shall have an internal baffle to provide separate working and outlet chambers. When two ( 2) tanks are used, the first shall be two-thirds (2/3) of the required size.

Minimum permitted size of the septic tank shall be:

Six (6) persons or less - 1,000 gallons.

Each additional person - 125 gallons increased capacity.

If the septic tank will be receiving materials from a garbage disposal, it is recommended the required tank size be increased by 250 gallons.

It is highly recommended, to help prolong the life of the disposal field, that all septic tanks be pumped as recommended on the design, or every three (3) years.

Page 14

Sewage Ordinance

5400.

5410.

5420.

5500.

5510.

5520.

5600.

5610.

SEWAGE DRAINS (BUILDING SEWERS)

The waste line from the building to the septic tank and from the septic tank to the dosing chamber (if applicable), shall be constructed of not less than four-inch (4") cast iron sewer service pipe, rubber ring jointed acrylonitrile-butadiene-styrene (ABS, or PVC) solid wall schedule forty sewer service pipe. Other materials may be proposed for acceptance by the permit granting authority. All joints shall be sealed to provide watertight conduit. The grade of the building sewer pipe shall be at least one-eighth inch (1/8") per horizontal foot, with one-quarter inch (1/4") per foot preferred.

If the septic tank is located more than forty feet (401) from the building, outside cleanouts shall be provided.

DISTRIBUTION BOXES

Where two or more lines are used for leaching, distribution boxes shall be recommended for septic systems. The distribution box shall be set on concrete and/or cement to secure and level. Said concrete and/or mortar mix shall extend to firm undisturbed earth. The distribution box shall be adjusted and tested with flowing water to determine that it is equally distributing the water out of each outlet pipe. All the holes around the inlet and outlet pipes shall be sealed and watertight.

All distribution boxes shall be accessible. Periodic checking of the distribution box for equal distribution is recommended.

LEACHING FACILITIES

All leaching facilities shall be sized according to Table 2 below and Table 1 (Section 5110). Table 2 shall not be used for leaching pits (seepage pits). Leaching pits (seepage pits) shall use Table 1 to calculate the number of people and use design flows of 80 gallons per day per person.

No subsurface leaching facilities shall be under parking lots or driveways.

Sewage Ordinance

Page 15

5611.

5620.

5621.

5630.

5631.

5640.

5641.

5700.

5710.

The construction of leaching facilities should be planned so that it is not necessary to operate heavy machinery over the leach lines once they are in place. Final grading should be done with a light machine having wide track or low pressure tires, fourteen (14) psi maximum. The installer shall verify the procedures are such that the lines are not broken or displaced or soil unnecessarily compacted. Bulldozers and backhoes shall not operate in the bottom of the bed area.

ABSORPTION TRENCHES

The required minimum six (6') feet on center for trench design shall be amended to eight (81) feet. Leaching lines shall be at least eight (8') apart on centerlines.

LEACHING BEDS ( SEEPAGE BEDS )

Not less than two lines shall be used.

LEACHING PITS (SEEPAGE PITS)

Leaching pits shall not be used for new construction. When constructed for an existing dwelling, they may be designed in accordance with the Wastewater System & Potable Water Supply Rules.

REQUIRED SIZE FOR LEACHING TRENCHES AND BEDS

The table below gives the minimum seepage areas on square feet required for residential installations, based on soils absorption. Square feet of effective areas shall be based on the bottom area of the trench or bed. Table 2 shall be used for calculating the minimum seepage area.

Table 2.

Sq. Feet Effective Seepage

Per Person Based on 80 Gallons

Per Day Per Person

95

128

148

188

240

270

two tests in each of the primary and

Slowest Percolation Rate* Time to Drop: One Inch (1")

5 minutes or less

to 10 minutes

to 15 minutes

to 30 minutes

to 45 minutes

to 60 minutes

*Based on a minimum of replacement fields.

Page 16

Sewage Ordinance

5800.

5810.

5900.

5910.

5920.

5930.

6000.

6010.

6020.

6030.

6040.

WATER SAVING DEVICES

Water conservation and water saving devices are encouraged. A 10% reduction may be granted for using water saving devices.

PUMPS

Whenever pumping is necessary to pump sewage in the disposal field, dual-alternating pumps shall be required for all commercial buildings. For single-family homes, the pump chamber shall be of sufficient size to hold one (1) full day's gallonage at maximum capacity (one-day storage reserve capacity).

In the case of pumping, a warning system shall be provided to alert occupants of the failure of a pump.

All designs requiring a pump shall include a pump curve for the pump being specified.

ALTERNATIVE SYSTEMS & PERMITTED DEVIATIONS

Chemical toilets, privies, composting toilets and incineration toilets may be approved on a case-by-case basis by the Sewage officer, but no reduction in the sewage disposal system is allowed.

Full replacement area for a disposal field is required. Reduction in the size of any mound system will not be permitted.

At the discretion of the Board of Selectmen, and authorized in writing, deviations from the design specifications in the Wastewater System & Potable Water Supply Rules may be allowed. Such deviation will only be allowed if the minimum soil and site requirements and the performance standards of the Wastewater System & Potable Water Supply Rules are met.

The Sewage Officer may approve innovative sewage disposal systems, which have an approved Innovative Systems Permit from the Department of Environmental Conservation.

Sewage Ordinance

Page 17

7000.

APPEALS

An applicant aggrieved by the decision of the Sewage Officer may appeal the decision in writing to the Board of Selectmen within thirty (30) days of such decision. The Board of Selectmen shall hold a hearing within thirty( 30) days of such appeal and shall render a- decision within fifteen (15) days after the close of such hearing. Following the Board of Selectmen's hearing, any person aggrieved by a decision of the Board of Selectmen may appeal that decision to Superior Court. The administrative process must be exhausted before the appeal to Superior Court.

8000.

ENFORCEMENT

A person who neglects or refuses to comply with the provisions of this ordinance may be fined not more than $500. for each offense by the Superior Court. Each week that a violation is continued shall constitute a separate offense (24 v SA, Section 1974).

9000.

SEVERABILITY

If any portion of this ordinance is held unconstitutional or invalid by a court of competent jurisdiction, the remainder of this ordinance shall not be affected.

As amended by the Dover Board of Selectmen of the Town of Dover, in Windham County, State of Vermont, at a meeting held on this 		 day of 		, 2002.

Charles Gentilin, Chairman			Robert Barry

Bruce Wyman, Vice Chair			John Mulhall

James Overton II